## Slide 1: WFPS – Wireless Fire Protection System
ZONE-3
MQTT - Protocol
HTTP - Protocol
Broker
Server
I-Dev’s
EoN
Sensor/Actuator
Hard Wire
Hard Wire
Serial
EoN
Sensor/Actuator
Hard Wire
Hard Wire
Serial
EoN
Sensor/Actuator
Hard Wire
Hard Wire
Serial
ZONE-1
ZONE-2
Notes: This is another option for an Overview slides using transitions.

## Slide 2: Server - HW
MQTT – Protocol
EoN
HTTP - Protocol
Server
Wemos D1
I-Dev’s

## Slide 3: EoN – Edge of Network
Server - Broker
MQTT - Protocol
Sensor/Actuator
Hard Wire
Hard Wire
Serial
ZONE-2
Wemos D1
EoN
Arduino Mega
Lcd Keypad
Notes: This is another option for an Overview slides using transitions.

## Slide 4
Server - Broker
MQTT - Protocol
Sensor/Actuator
Hard Wire
Hard Wire
Serial
EoN – Edge of Network
c/w Local Panel
ZONE-2
Wemos D1
EoN
Arduino Mega
Lcd Keypad
Notes: This is another option for an Overview slides using transitions.

## Slide 5: LocalPanel
File : aLocalPanel.ino
exp = NO_EXCEPTION;
lifeLed.blink(BLINK_NORMAL);
locPan.menu();
fpSys.execute();
commSer.execute();
LOCAL_OPERATION_EXCEPTION
LOCAL_PARAMETER_EXEPCTION
commSer. sendValue();
fpSys.updateParameter();
locPan.updateParameter();
commSer.sendParameter();
1
Setup Serial, Serial1
Setup lifeLed
Setup locPan
Setup fpSys
Setup commSer
Start

## Slide 6: LocalPanel
REMOTE_OPERATION_EXCEPTION
REMOTE_PARAMETER_EXCEPTION
fpSys.execute();
fpSys.updateParameter();
locPan.updateParameter();
fpSys.execute();
1
End
File : aLocalPanel.ino

## Slide 7: _fpSys->execute()
(operationMode = MODE_AUTO ) & (sensorStatus != NO_ALARM)
Yes
No
operationMode = MODE_AUTO_ON
File : fpSys.cpp
sensorStatus = _fireSensor->getStatus()
operationMode = _pbAMRT->getCmd(DEBOUNCING_TIME)
this->_logicOperation(operationMode, sensorStatus)
_ledAMR->status(operationMode)
Update parameter(sensor value, alarm, operationMode)
Update exception
return

## Slide 8: _fireSensor->getStatus()
Val > Setting
Yes
No
statusAi = HIGH_ALARM
return (statusAi)
File : src\ioDevices\analogInput.cpp
getValue from sensor
(with AlfaEMA filter)
statusAi = NO_ALARM

## Slide 9: _pbAMRT->getCmd(DEBOUNCING_TIME)
File : src\compDevices\pbAMRT.cpp
_pbTest = active
cmd = MODE_TEST
Yes
No
_pbReset = active
_prevCmd = MODE_RESET
Yes
cmd = MODE_READY
Yes
_prevCmd = MODE_READY
cmd = MODE_READY
Yes
cmd = MODE_RESET
_pbAuto = active
cmd = MODE_AUTO
Y
3
2
getData from P/B with debouncing mechanism

## Slide 10: _pbAMRT->getCmd(DEBOUNCING_TIME)
_pbManual = active
cmd = MODE_MANUAL_ON
Y
cmd = MODE_MANUAL
_prevCmd = cmd
return (cmd)
2
_prevCmd = MODE_MANUAL
Y
3
cmd = MODE_MANUAL_ON
_prevCmd = MODE_MANUAL_ON
Y
File : src\compDevices\pbAMRT.cpp

## Slide 11: _ledAMR->status(operationMode)
File : src\compDevices\ledAMR.cpp
State = MODE_TEST
Y
State = operationMode
State = MODE_AUTO
State = MODE_AUTO_ON
State = MODE_MANUAL
_ledAuto->on();
_ledManual->on();
_ledReset->on();
_ledAuto->on();
_ledManual->off();
_ledReset->off();
_ledAuto->blink();
_ledManual->off();
_ledReset->off();
_ledAuto->off();
_ledManual->on();
_ledReset->off();
4

## Slide 12: _ledAMR->status(operationMode)
File : src\compDevices\ledAMR.cpp
State = MODE_RESET
Y
State = MODE_READY
_ledAuto->blink();
_ledManual->blink();
_ledReset->off();
_ledAuto->off();
_ledManual->off();
_ledReset->blink();
State = MODE_MANUAL_ON
_ledAuto->off();
_ledManual->blink();
_ledReset->off();
4

## Slide 13: this->_logicOperation(operationMode, sensorStatus)
File : aLocalPanel.ino
State = MODE_TEST
Y
State = MODE_AUTO
State = MODE_MANUAL
sensorStatus = ALARM
5
State = operationMode
_buzzer->on();
_ solenoidValve- >on();
_ solenoidValve- >off();
_ solenoidValve- >off();

## Slide 14: this->_logicOperation(operationMode, sensorStatus)
State = MODE_READY
Y
State = MODE_RESET
5
State = MODE_MANUAL_ON
_ solenoidValve- >off();
_ solenoidValve- >off();
_ solenoidValve- >on();
return
File : aLocalPanel.ino

## Slide 15: _locPan->menu()
_modeMenu = MODE_MENU_MAIN
File : locPan.cpp
this->_menuMain(key)
this->_menuParameter(key)
_modeMenu = MODE_MENU_PARAMETER
this->_menuChangeParameter(key)
_modeMenu = MODE_CHANGE_PARAMETER
Key = this->_getCommand()
return

## Slide 16: this->_menuMain(key)
_menuIndex = 0
File : locPan.cpp
idx = this->_increaseIndex();
key = UP
key = DOWN
idx = this->_decreaseIndex();
21
this->_sendMenu(idx);
this->_viewMenu(idx);
Start

## Slide 17: this->_menuMain(key)
File : locPan.cpp
_modeMenu = MODE_MENU_PARAMETER;
this->updateParameter();
this->_initPrevIndex();
this->_paramIndex = PARAMETER_VALUE;
this->menu();
key = RIGHT
21
menuData.isHasParam
menuData = _accessMenu->read(this->_menuIndex);
return

## Slide 18: this->_menuParameter(key)
_paramIndex = PARAMETER_VALUE
File : locPan.cpp
idx = this->_increaseIndex();
key = UP
key = DOWN
idx = this->_decreaseIndex();
22
this->_sendParameter(idx);
this->_viewParameter(idx);
Start

## Slide 19: this->_menuParameter(key)
File : locPan.cpp
key = LEFT
22
_modeMenu = MODE_MENU_MAIN;
this->_menuIndex = 0;
this->menu();
23

## Slide 20: this->_menuParameter(key)
File : locPan.cpp
_modeMenu = MODE_CHANGE_PARAMETER;
this->_isParamChanged = true;
this->menu();
key = RIGHT
23
_accessParameter->isChangeAble(this->_paramIndex)
return